MAJ20—0001 Plat Santa Fe Park F1 DW plan 20998

Plan Review Coordinator at 303.628.6100 #2 or email watersalesplanreview@denverwater.org

Site specific comments if any:

Denver Water plan 20998 is still in review, likely 3 more submittals will be needed, and the easement approval prior stamping approve the plan.

Review attached PDF and comments from Denver Water Property section.

These are Denver Water Property comments and attached redlines.

Prop 1) In cases which the water line does not meet the 10' minimum distance from water line to easement line there will need to be a variance request that will need to be submitted, or the water line will have to be moved slightly to maintain the 10' minimum distance. See dimensions provided throughout the Water Only sheets. Apply to all.

Prop 2) See Prop 1 comment.

Prop 3) Hydrants must have 5' of distance on all sides from center nut. Hydrant will either need to be moved slightly to provide for the 5' minimum or a variance request will need to be submitted. Prop 4) See Prop 1 comment.

Prop 5) See Prop 1 comment.

Prop 6) The linework or the easement location looks off.

Prop 7) See Prop 8 comment.

Prop 8) These are private drives with domestic lines, is the district/others okay with the distance between water line and easement boundary?

Prop 9) See Prop 8 comment.

Prop 10) Blow off requires 5' of distance on all sides. Blow off will need to be moved further into the easement to provide the 5' minimum distance.

Prop 11) See Prop 3 comment.

Prop 12) See Prop 8 comment.

Prop 13) See Prop 1 comment.

Prop 14) See Prop 10 comment.

Prop 15) See comments on previous sheets.

Prop 16) Was this easement also included in the easement package?

Prop 17) Waterline may need variance in this location due to lack of the 10' minimum distance.

Prop 18) See Prop 3 comment.

Prop 19) See Prop 1 comment.

Prop 20) Submit easement documents for review.

Prop 21) Possible license for Dad Gulch crossing?

Prop 22) Does retaining wall encroach into 50' easement? Will need to be written into special provisions section of the 50' easement form and will need to be expressly approved by the district. Will need Exhibit B plan and profile showing water line in relation to the wall.

Prop 23) Distance between retaining wall and water line seems too close.

Prop 24) Concerns about other encroachments into the 50' easement. Is district OK with these?

Prop 25) Submit documents proposing ROW.

Prop 26) Clearly dimension existing ROW.

Prop 27) See Prop 25 comment.

Prop 28) See Prop 25 comment, clearly dimension existing Santa Fe ROW.

Prop 29) Was this easement included in the submittal?

Prop 30) Gate will need to be written into special provisions section of easement document and expressly approved by the district. Exhibit B plan and profile needed to show water line in relation to gate and other utilities.

Prop 31) Clearly dimension existing Santa Fe ROW lines. Plat looks okay, please see redlines for submitted easement documents. Sent PDFs of easement redlines to Ana to send to all appropriate parties.