Southwest Metropolitan

Water and Sanitation District

8739 W. Coal Mine Ave.  • Littleton, Colorado   80123 • (303) 979-2333 •

May 4, 2022

Justin Montgomery jmontgomery@littletongov.org

Planning Services

City of Littleton Community Development

2255 W. Berry Ave.

Littleton, CO 80120

Re: Toll Brothers – RE: SDP21-0009 & MIN21-0009 Toll Brothers Santa Fe

Dear Justin,

Thank you for providing Southwest Metropolitan Water and Sanitation District (SWM) the opportunity to comment on the proposed Santa Fe Park South development. District staff has reviewed both the proposed Minor Sub Plat and Site Development plan and provides the following comments:

This document is intended to help guide developers on issues that are more likely to impact project success. All developments are required to have approved water and sewer plans in accordance with Southwest Metropolitan Water and Sewer Standards and this is not intended as a substitute. Water Plans shall also be subject to review and approval from Denver Water.

Water plan submittal: Water plan review and approval is required for all pipe installations 3” diameter and larger pipe connecting to a public water system controlled by Southwest Metropolitan Water and Sanitation District (District). Water plans must be in accordance with District and Denver Water Engineering Standards.

Sewer plan submittal: Sewer plan review and approval is required for all pipe installations 8” diameter and larger connecting to a public sewer system controlled by the District. Sewer design must be in accordance with the District Engineering Standards.

Details on the District’s Water and Sewer Plan Review Processes are located at: https://swmetrowater.org/construction-corner/new-development-project/plan-submittal-procedures/

Details on Denver Water Plan Review process is located at : https://www.denverwater.org/contractors/construction‐information/plan‐   reviews

Application and Agreement

The process of plan submittal and review begins with the application and agreement which is a contract between the District and the owner that sets forth the terms and conditions pursuant to which such sewer and water mains will be conditionally accepted by the District and allowed to connect to the District public water and sanitary sewer systems.

Requirements for Water and Sewer Plan Submittal:

  - All plans and specifications submitted to the District for review, comment, and approval of a water or sewer system extension or modification shall be prepared by, or under the direct supervision of a professional engineer registered by the State of Colorado. Said professional engineer shall be responsible for the design, the plans, determining the material specifications and conducting the field survey. All submitted plans and specifications shall include the professional engineer's seal prior to approval for construction

  - All plans must be approved by the District manager, District engineer, and in the case of water plans, Denver Water and/or the City of Littleton prior to initiation of construction. Plans shall be submitted and reviewed in accordance with the District’s procedures and requirements.

  - Pipe installation contractor must be qualified by the District.

  - Regarding sewer plans, see District Engineering Standards regarding required flow in pipe, diameter, slope, and pipe length between manholes.

  - Water distribution mains that dead‐end and are not looped, may cause water quality and/or fire protection issues and are therefore only permitted in limited circumstances as required. The Developer is responsible for all necessary water distribution system modifications needed to meet the required fire flows, as directed by the governing Fire District.

Easements for Water or Sewer:

- If a water easement is required, the easement will be granted to the District according to Denver Water Standards.

- District water easement documents must be in compliance with Denver Water Engineering Standards and easement template – any modification of the Denver Water easement document must be submitted as a “Special Provision” in writing with description and location (northing and easting) as an exhibit for review.

- Easement widths require a minimum of 30 or 50 feet, depending on easement type. Non‐exclusive allows other utilities in easement.

- If water or sewer facility is installed within a dedicated public street right-of-way, a copy of the recorded plat must be submitted showing such public use dedication.

- Water and sewer mains installed in platted private roadways tracts will require an easement.

- The easement must follow the radius of the curbs in the roadway for delamination. The cross slope of easements must not exceed 4%.

- Easements are granted to the District and must be recorded prior to final plat recording and must be included on the final plat.

Tips to ensure a smooth plan review process

- Schedule a pre‐design meeting with our staff. Requests can be scheduled by sending an email to info@swmetrowater.org - Have the following information prior to meeting:

- For water plans, please meet with the local fire department regarding emergency access, hydrant locations and site fire flow estimates.

- Infrastructure Master Plan – for large, redeveloped areas

- Number of taps for sewer and water

- Type of building (e.g., residential, commercial, industrial, manufacturing, mixed use, etc.).

- All points of connection for water and sewer mains

- Location of fire hydrants and large taps

- Requirements for easements and/or dedicated public right‐of‐way

- Access to proposed manholes

- Separation of sewer and water mains

Fees:

- Plan Review Fee for Water

- $5.00/lineal foot for water or sewer (main line pipe only)

- Minimum deposit $2,000

- Construction Inspection Fee for Water

- $5.00/lineal foot for water (main line pipe only)

- $3.00/lineal foot for Sewer (main line pipe only)

- $4.00 Sewer Inclination Survey

- Minimum deposit $2,000

- Easement Processing Fee

- $2,000 deposit

Reimbursement of unused fees: Actual costs are reconciled against initial deposit each month and if the deposit will not be sufficient to complete the process, an additional deposit will be required; any remaining funds once the account is reconciled will be returned to the applicant.

Tips for Conditional Acceptance and Service Tap Application

- In order to obtain Conditional Acceptance which releases the project for sewer and water service tap permits, the following is needed upon completion of construction:

- As-builts of the project stamped by an engineer

- Easement certification stamped by a licensed surveyor – ensures the sewer and/or water main is within the easement boundary.

- Copy of recorded subdivision plat

- All fees are paid and current

- Sewer and water construction cost

- Address, block and lot number of all sewer and/or water taps